## Cover Sheet
Extensive Urban MEN System supplied by a Buried Cable.
HB 219 Worked Example 3.7.1
1 km underground HV feed to a pad mounted distribution transformer, common HV/LV earth, extensive MEN, LV neutral bonded to HV source substation via HV cable sheath.
Extensive Urban MEN system supplied by a 11kV buried cable. HV single phase-to-earth fault at the pad mounted distribution transformer.
HV Fault Source Data
HV phase - neutral voltage | 6350 | V
Single phase fault level | 200 | MVA
HV Cable Data
Cable size and type | 150 sqmm Al Belted PILCPS
Length | 1 | km
Positive sequence cable impedance | 0.2078 | + j | 0.0773 | W / km
Zero sequence impedance of cable conductor (Zcond0) | 0.2062 | + j | 0.1142 | W / km
Zero sequence sheath resistance (Rsh0) | 2.6612 | W / km
Effective zero sequence impedance of the general mass of earth (Zg0) | 0.148 | + j | 2.0779 | W / km
NER and Earth Impedance Data
Neutral Earthing Resistor resistance | ZNER = | 0 | W
Zone Substation earthmat resistance | RZS = | 0.01 | W
Surface soil resistivity | r = | 10 | W - m
Impedance of typical urban extensive MEN system
Each customer has one 1.8m deep copper clad 12mm diameter electrode. 4 customers are supplied from each pole, and the LV span length between poles is 50m. The deep layer soil resistivity is assumed to be 100 Ω-m. The LV neutral is a DOG conductor with a self impedance of 0.322 + 0.757j Ω/km. The MEN system extends in both directions from the distribution transformer.
MEN impedance of typical urban extensive MEN system (see HB219 Worked Example 4.1.1 for the derivation of this value). | ZMEN = | 0.103 | +j | 0.076 | Ω
Description of distribution transformer earthmat | 4 x 1.8m earth rods (12mm dia.) at 1.8m spacing, connected by bare 16mm2 earth wire
Distribution transformer earthmat earth resistance formula | Re = | 0.1346 | r
Assumptions Made
1. Source impedance is purely reactive.
2. Positive sequence source impedance = negative sequence source impedance = zero sequence source impedance
Calculated Values
Equivalent hemispherical radius of the distribution transformer earthmat |  |  |  | 1.1824 | m
Fault current (returning through the earth) |  |  |  | 3599.8522 | A
EPR on the distribution transformer earthmat |  |  |  | 427.4527 | V

## Calculations
Calculations
Symmetrical components network for a HV single phase-to-earth fault at the pad mounted distribution transformer
HV Fault Source Data
HV phase - neutral voltage | VS1 = | 6350 | V
Single phase fault level | S = | 200 | MVA
Assume source impedance is purely reactive.
Positive sequence source impedance | ZS1 = |  | = | 0.6048375j | Ω |  | 0.60484
Negative sequence source impedance | ZS2 = | ZS1 | = | 0.6048375j | Ω
Zero sequence source impedance | ZS0 = | ZS1 | = | 0.6048375j | Ω
HV Cable Data
Cable size and type |  | 150 sqmm Al Belted PILCPS
Length | C = | 1 | km
Positive sequence cable impedance | ZC1 = | 0.2078+7.73E-002j |  | W / km
Negative sequence cable impedance | ZC2 = | ZL1 = | 0.2078+7.73E-002j |  | W / km
Zero sequence impedance of cable conductor (Zcond0) | Zcond0 = | 0.2062+0.1142j |  | W / km
Zero sequence sheath resistance (Rsh0) | Rsh0 = | 2.6612 |  | W / km
Effective zero sequence impedance of the general mass of earth (Zg0) | Zg0 = | 0.148+2.0779j
NER and Earth Impedances
Neutral Earthing Resistor resistance | ZNER = | 0 | Ω
Zone Substation earthmat resistance | RMATZS = | 0.01 | Ω
Surface soil resistivity | r = | 10 | Ω - m
Impedance of typical urban extensive MEN system
Each customer has one 1.8m deep copper clad 12mm diameter electrode. 4 customers are supplied from each pole, and the LV span length between poles is 50m. The deep layer soil resistivity is assumed to be 100 Ω-m. The LV neutral is a DOG conductor with a self impedance of 0.322 + 0.757j Ω/km. The MEN system extends in both directions from the distribution transformer.
MEN impedance of typical urban extensive MEN system (see HB219 Worked Example 4.1.1 for the derivation of this value). | ZMEN = | 0.103+7.6E-002j |  | Ω
Description of distribution transformer earthmat |  | 4 x 1.8m earth rods (12mm dia.) at 1.8m spacing, connected by bare 16mm2 earth wire
Distribution transformer earthmat earth resistance | Re = | 0.1346 | r
| = | 1.346 | Ω
Equivalent Hemispherical Radius | rE =
| = | 1.1824 | m
Equivalent MEN plus Re impedance | Zeq =
| = | 9.91085957526847E-002+6.53994111268433E-002j
Network Impedances
Sequence network impedances | Zpos = | ZS1 + ZC1.C
| = | 0.2078+0.6821375j |  | Ω
| Zneg = | ZS2 + ZC2.C
| = | 0.2078+0.6821375j |  | Ω
| Zzero = | [5 empty] | 1.18126388635021+1.07300890534338j
2.6612
| = | 1.38746388635021+1.79204640534338j |  |  |  | Ω | 0.475325787258054+2.27409823338053j
Fault Current
Zero sequence fault current | I0 =
| = | 866.503098813751-1516.84158242355j |  |  |  | A
Zero sequence fault current returning via the earth | Ig0 =
| = | -129.72166594457-1192.91829928194j |  |  |  | A
Fault current (returning through the earth) | If = | 3.Ig0
| │If │ = | 3599.8522 | A
EPR
EPR on the distribution transformer earthmat | EPRdt = | If.Zeq
| = | 427.4527 | V